20250327 Site meeting at Napier Pump Station
Present: Councillor Ross, H Krohn, B Neale, S Peck, J Moult.
This serves to confirm what was discussed at this morning’s meeting:
1.      Of the two failed sewage pumps sent to Cape Town only one is repairable. This repair work is to be undertaken by a non-contracted maintenance workshop. The cause of the pump failures needs to be investigated.
2.      The repairable pump will be back in Napier by Saturday morning for installation.
3.      CAM has called for tenders to supply 2 new pumps, similar to the existing pump for immediate purchase. One pump will be for operational standby duty and the other a non-installed spare. 
4.      The building of a closed sump to capture possible future spills will be undertaken in the 2025/26 financial year.
5.      The preliminary redesign of the pump station has been undertaken by CAM’s consultants for building in 2026/27.
6.      There was still at least one pool of sewage within the pump station perimeter, an indication of possible further overflowing of the pump sump.
7.      Despite having been issued with protective clothing CAM employees working at the pump station were not using these.
8.      The poor state of the pump station was as a result of years of neglect.
9.      CAM Administration need to be held accountable for the poor performance of the pump station.
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